## Slide 1: Detention Basics

## Slide 2: Detention Basics-UG

## Slide 3: Objectives
Students should have the ability to:
Name the advantages of a detention basin
Develop an inflow hydrograph
Develop a stage-storage curve
Develop an outflow curve for single or multi-staged outlets

## Slide 4: Detention Basin Elements

## Slide 5: Detention Basin-Purposes
Store water temporarily during a storm and release the stored water slowly (attenuate the flow)
Store first-flush
Allow and/or Design for infiltration
  If all water is infiltrated then (retention basin)

## Slide 6: Detention Basins (location)
On-Site?
Or
Regional?
Discussion

## Slide 7: Detention Basin Components
Inflow (ditch or pipe)
Storage
Outflow (single/multiple stage)
  Orifice
  Weir
Emergency spillway

## Slide 8: Routing
Method used to model the outflow hydrograph
Based on continuity equation
  Water in varies
  Water out varies
  Storage

## Slide 9: Information Needed to Route
Inflow hydrograph
Table or graph of storage volume to water elevation in the proposed detention basin
Table or graph of outflow to water elevation (discharge rating)

## Slide 10: Inflow hydrograph (3 methods)
1. Ch 5 of TR-55 (NRCS method)
Rational method:
2. Simple symmetrical triangle
(base = 2*tc and peak occurs at tc)
3. Asymmetrical triangle
(total base = 2.67 tc and peak occurs at tc)

## Slide 11: TR-55 Hydrograph (NRCS Method)
Peak flow is higher after development
Peak flow occurs earlier after development

## Slide 12: Rational Method: Simple Symmetrical Triangle

## Slide 13: Rational Method: Time base of 2.67 tc
Area under hydrograph?

## Slide 14: Computing Storage Volumes
Two Methods:
  Elevation-Area (detention basins)
  Average End-Area (pipes)

## Slide 15: Elevation-Area
15
Elevation-Area (detention basins)
  Contour lines are determined around basin
  Determine area of each contour
  Volume between 2 contours = average area*depth between the contours
  Prepare a table showing elevation, area, incremental volume and cumulative volume

## Slide 16: Plan and Profile-Detention Basin

## Slide 17: Elevation-Area Method
Elev (ft) | Area (ft2) | Incr. Vol (ft3) | Cum. Vol (ft3)
230 | 0 | 0 | 0
231 | 250 | (250/2*1)=125 | 125
232 | 840 | ((250+840)/2*1)= 545 | 670
233 | 1350 | 1095 | 1765
234 | 2280 | 1815 | 3580
235 | 3680 | 2980 | 6560
236 | 5040 | 4360 | 10,920

## Slide 18: Water Volume versus Elevation

## Slide 19: Computing Storage Volumes when Underground Pipes are Used
Average end-area (pipes)
  Find u/s area at elevation increments
  Find d/s area at elevation increments
  Average the areas & multiply by length
  This gives you total volumes (not incremental volumes)

## Slide 20: Sloped Pipe Water Volumes at Various Elevations

## Slide 21: End Area Method

## Slide 22: Pipe used as Detention Basin

## Slide 23: Break

## Slide 24: Discharge Rating
Calculate outflows based on water elevation in the detention pond
Orifice and weir equations are used
  Single stage
  Multi stage
If more than one stage, calculate each outlet separately and add to get stage-discharge curves

## Slide 25: Orifices
25
Hole in a wall through which water flows
  Square edge
  Beveled edge

## Slide 26: Orifice
26
When water flows through an orifice the water contracts with a smaller area than the original orifice opening (vena contracta)
www.spiraxsarco.com
www.diracdelta.co.uk

## Slide 27: General Orifice Equation
27
Q=ca(2gh).5
Where:
  Q=discharge (cfs or cms)
  c=discharge coefficient (0.62 often used)
  a=cross-sectional orifice area (sq ft or sq meters)
  h=total head (ft or m)
  g=gravitational constant (32.2 or 9.81)

## Slide 28: Orifice Discharge
28
Free Discharge
Submerged Discharge
Equation is the same. Head for the submerged discharge is the difference between upper and lower water surfaces

## Slide 29: Orifice-Free Discharge
29
Given: Dia=6”, WSE=220.0 ft;
Elev of orifice centerline=200.0 ft
Q=ca(2gh).5
Q=0.62*0.196*(2*32.2*20).5
Q=4.4 cfs

## Slide 30: Weir
30
Horizontal surface over which water is allowed to flow
Used to regulate and measure flows
http://www.flow3d.com/appl/weir.htm

## Slide 31: Rectangular, Sharp-Crested Weir
31
Q=cLH3/2
  Q-flow (cfs)
  c-adjusted discharge coefficient (careful)
    c=3.27+0.4(H/P) where P is ht of weir above channel bottom
  L-effective crest length, ft
    L=L’-0.1nH
      L’=actual measured crest length and n=# of contractions
  H-head above crest, ft

## Slide 32: Rectangular, Broad-Crested Weir
32
Q=cLH3/2
  Q-flow (cfs)
  c-discharge coefficient
  L-crest length, ft
  H-head above crest, ft

## Slide 33: V-Notch or Triangular Weir
33
Q=c*tan(angle/2)*H5/2
  c = 2.5 (but should calibrate)

## Slide 34: Other Weir Types
34
Cipoletti (trapezoidal)
Ogee (dam spillway)
www.lmnoeng.com
youngiil.co.kr

## Slide 35: Detention Outlet Structures
35
Single Stage (culvert or orifice)
Multi-Staged to handle different flows
Combination of orifices &/or weirs

## Slide 36: Single Stage Outlet Example
36
An outlet consisting of a 12” pipe is proposed for a detention basin. The invert of the pipe is 320.0 feet and the top of berm is 325.0 ft. Compute the discharge rating for the outlet.
Area=0.785 sq ft
Assume c=0.62
Use orifice equation: Q=ca(2gh).5

## Slide 37: Single Stage Outlet Example
37
WSE (ft) | h (to c/l of pipe) | Q out (cfs)
320 | 0 | 0
321 | 0.5 | 2.8
322 | 1.5 | 4.8
323 | 2.5 | 6.2
324 | 3.5 | 7.3
325 | 4.5 | 8.3

## Slide 38: Single State Outlet
38
Chart: Stage-Discharge Curve
| 322 | 323 | 324 | 325 | 326 | 327
 | 0 | 2.7632 | 4.786 | 6.1787 | 7.3107 | 8.2895

## Slide 39: Multi-Stage (Three-Stage Outlet)
39
4” Orifice and 2 weirs L=1.5’ and L=12.5’

## Slide 40: Multistage Outlet

## Slide 41: Multi-Stage Outlet
41
Chart: Stage-Discharge Curve
| 560 | 561 | 562 | 562.66999999999996 | 563 | 563.66999999999996 | 564 | 565
 | 0 | 0.39636 | 0.5879 | 0.68698 | 1.5839 | 5.7927 | 15.2657 | 82.3204

## Slide 42: Emergency Spillway
Emergency Outlet
  Rainfall exceeds design storm
  or outlet becomes blocked
Purpose
  Prevent overtopping of berm
  Control direction of overflow

## Slide 43: Emergency Spillway Typical Design Criteria
Spillway crest set at or above the maximum impoundment elev
Designed for emergency spillway design storm (minus what can be handled by outflow structure) or designed to convey peak discharge of design storm (assuming outflow structure plugged)
Top of berm = WSE through the spillway + freeboard (1-2’ typical)