## Slide 1: CTC 261 Hydraulics Storm Drainage Systems

## Slide 2: Objectives
Ability to:
Understand the steps for storm drainage design
Design riprap downstream of pipe outlet

## Slide 3: References:
Urban Drainage Design Manual 4th Edition
HEC-22 (hydraulic engineering circular)
Publication Year: 2024

## Slide 4: Two Concerns
Preventing excess spread of water on the traveled way
  Design of curbs, gutters and inlets
Protecting adjacent natural resources and property
  Design of outlets

## Slide 5: Gutter Capacity
Q is determined via rational method
Slopes are based on the vertical alignment and pavement cross slope (normal and superelevated values)
Usually solving for width of flow in gutter and checking it against criteria

## Slide 6: Gutter Capacity Calculation
Modified form of Manning’s equation
  Manning’s roughness coefficient
  Width of flow (or spread) in the gutter
  Gutter cross slope
  Gutter longitudinal slope
Equation or nomograph
Inlets placed where spread exceeds criteria

## Slide 7: Gutter Capacity Equation
Q=(0.376/n)*Sx1.67S0.5T2.67
Where:
Q=flow rate (cms)
N=manning’s roughness coefficient
Sx=cross slope (m/m)------decimal
S=longitudinal slope (m/m)-----decimal
T=width of flow or spread in the gutter (m)

## Slide 8: Gutter Flow Nomograph

## Slide 9: Spread
Interstates/freeways-should only encroach on shoulder
For other road classifications, spread should not encroach beyond ½ the width of the right most travel lane
Puddle depth <10 mm less than the curb height
Can utilize parking lanes or shoulder for gutter flow

## Slide 10: Inlets
Curb-opening inlet
  No grate (not hydraulically efficient; rarely used)
Gutter Inlet
  Grate only-used if no curb (common if no curb)
  Slotted (rarely used)
Combination Inlet
  Used w/ curbs (common for curbed areas)

## Slide 11: Grates
Reticuline
Rectangular
Parallel bar

## Slide 12: Interception Capacity
Depends on geometry and characteristics of gutter flow
Water not intercepted is called carryover, bypass or runby
On-grade (percent efficiency)
Sag location
  Acts as a weir for shallow depths and as an orifice for deeper depths

## Slide 13: Factors for Inlet Location
Drainage areas/spread
Maintenance
Low points
Up-grade of intersections, major driveways, pedestrian crosswalks and cross slope reversals to intercept flow

## Slide 14: Storm Drainage System Layout Basic Steps
Mark the location of inlets needed w/o drainage area consideration
Start at a high point and select a trial drainage area
Determine spread and depth of water
Determine intercepted and bypassed flow
Adjust inlet locations if needed
With bypass flow from upstream inlet, check the next inlet

## Slide 15: Design
Software
By hand w/ tables
  Hydrology
    Areas, runoff coefficients, Time of Conc, Intensity
  Hydraulics
    Pipe length/size/capacity/Velocity/Travel time in pipe

## Slide 16: Calculations

## Slide 17: Closed Systems - Pipes
Flow can be pressurized (full flow) or partial flow (open channel)
Energy losses:
  Pipe friction
  Junction losses

## Slide 18: Closed Systems – Pipes-2
18” minimum
Use grades paralleling the roadway (minimizes excavation, sheeting & backfill)
Min. velocity=3 fps
At manholes, line up the crowns (not the inverts)
Never decrease the pipe sizes or velocities
Use min. time of conc of 5 or 6 minutes

## Slide 19: Example-1

## Slide 20: Example-2

## Slide 21: Summary Data for Each Inlet
Inlet | Incr. DA (acres) | Incr. Tc (min) | Incr C
1 | .07 | 6 | 0.95
2 | .46 | 10 | 0.45
3 | .52 | 10 | 0.48
4 | .65 | 9 | 0.41
5 (MH) | n/a | n/a | n/a
6 | .10 | 6 | 0.95
7 | .15 | 6 | 0.95
8 | .70 | 14 | 0.38

## Slide 22: Pipe Segment 1-2
From IDF curve in Appendix C-3 & tc=6 min; i=5.5 in/hr
Q=CIA
Q=(0.95)(5.5)(0.07)
Peak Q = 0.37 cfs

## Slide 23: Pipe Segment 2-3

## Slide 24: Pipe Segment 2-3 (hydraulic path)
Find longest hydraulic path- see previous
Path A: 6 min+0.1min=6.1 minutes
  Travel time from table
Path B: 10 minute
Using IDF and tc=10 min, i=4.3 inches/hr
Area=Inlet areas 1+2 =.07+.45=0.53 acres

## Slide 25: Pipe Segment 2-3 (cont.)
Find composite runoff coefficient:
(0.95*.07+0.45*.46)/0.53=0.52
Q=CIA
Q=0.52*4.3*0.53
Qp=1.2 cfs

## Slide 26: Hydraulic Paths for Segment 3-5

## Slide 27: Pipe Segment 3-5
Find longest hydraulic path- see ovrhd
Path A: don’t consider
Path B: 10 min+0.6 min=10.6 minutes
Path C: 10 minutes
Using IDF and tc=10.6 min, i=4.2 inches/hr
Area=Inlet areas 1+2+3 =.07+.45+0.52 = 1.05 acres

## Slide 28: Pipe Segment 3-5 (cont.)
Find composite runoff coefficient:
(0.95*.07+0.45*.46+0.48*0.52)/1.05=0.50
Q=CIA
Q=0.50*4.2*1.05
Qp=2.2 cfs

## Slide 29: Pipe Table (using App A charts) (25-yr storm; n=0.015)
Pipe Seg | Qp (cfs) | Length (ft) | Slope (%) | Size (in) | Capacity (full-cfs) | Vel. (fps) | Travel Time (min)
1-2 | .37 | 30 | 2 | 12 | 4.4 | 3.4 | 0.15
2-3 | 1.2 | 200 | 3.25 | 12 | 5.8 | 5.6 | 0.6
3-5 | 2.2 | 25 | 2.5 | 12 | 5.0 | 6.0 | 0.1

## Slide 30: Storm System Outfalls

## Slide 31: Storm System Outfall
Point where collected stormwater is discharged from the system to the receiving body of water.
  Outfall at stream bank (headwall in bank)
  Channel connecting outfall with stream (headwall located outside of bank)
  Outfall discharged onto stream overbank (similar to 2 but no channel; use for wetlands)
    (See page 292 of your book)

## Slide 32: Permissible Velocities (based on soil texture) – See Appendix A-2
Values range from:
2.5 fps for Sand/Sandy Loam (noncolloidal)
To 6 fps for shale
If velocities are outside range then erosion control measures are warranted

## Slide 33: Outfall Erosion Control
Reduce Velocity
Energy Dissipator
Stilling Basin
Riprap
Erosion Control Mat
Sod
Gabion

## Slide 34: Erosion Control-Riprap
Various Design Methods/Standards
  Type of stone
  Size of stone
  Thickness of stone lining
  Length/width of apron

## Slide 35: From class book (out of print):

## Slide 36: Erosion Control-Riprap Type of stone
Hard
Durable
Angular (stones lock together)

## Slide 37: Riprap-Basic Steps
Determine velocity and compare to Appendix A-2
Determine TW (use culvert)
Determine type of stone
Determine median stone size
Determine apron length
Determine apron width
Provide plan/section

## Slide 38: Erosion Control-Riprap Size of Stone
D50 = (0.02/TW)*(Q/D0)4/3
TW is Tailwater Depth (ft)
D50 is Median Stone Size (ft)
D0 is Maximum Pipe or Culvert Width (ft)
Q is design discharge (cfs)

## Slide 39: Erosion Control-Riprap Length of Apron
TW > ½ Do
TW < ½ Do
See page 295 for equations

## Slide 40: Erosion Control-Riprap Width of Apron
Channel Downstream
  Line bottom of channel and part of the side slopes (1’ above TW depth)
No Channel Downstream
  TW > ½ Do
  TW < ½ Do
  See page 295-296 for equations