## Slide 1: CTC 450 Review
Friction Loss (2 types)
  Over a pipe length
    Darcy-Weisbach (Moody’s diagram)
    For iterative problems go back to the energy equation and derive relationship between v and f
  Connections/fittings, etc. (K*velocity head)

## Slide 2: Objectives
Determine how water distributes into 2 parallel pipes
Set up a spreadsheet to solve a simple water distribution system using the Hardy-Cross method

## Slide 3: Pipe Systems
Water municipality systems consist of many junctions or nodes; many sources, and many outlets (loads)
Object for designing a system is to deliver flow at some design pressure for the lowest cost
Software makes the design of these systems easier than in the past; however, it’s important to understand what the software is doing

## Slide 4: Pipes in Series

## Slide 5: Pipes-Parallel & Equivalence

## Slide 6: Two parallel pipes
If a pipe splits into two pipes how much flow will go into each pipe?
Each pipe has a length, friction factor and diameter
Head loss going through each pipe has to be equal

## Slide 7: Two parallel pipes
f1*(L1/D1)*(V12/2g)= f2*(L2/D2)*(V22/2g)
Rearrange to:
V1/V2=[(f2/f1)(L2/L1)(D1/D2)] .5
This is one equation that relates v1 and v2 What is the other equation?

## Slide 8: Determining flow distribution
What do you do for complex pipe systems?
Hardy-Cross (one method)
https://en.wikipedia.org/wiki/Hardy_Cross_method

## Slide 9: Hardy-Cross Method---Rules
Q’s into a junction=Q’s out of a junction
Head loss between any 2 junctions must be the same no matter what path is taken (head loss around a loop must be zero)

## Slide 10: Steps
Choose a positive direction (CW=+)
# all pipes or identify all nodes
Divide network into independent loops such that each branch is included in at least one loop

## Slide 11: 4. Calculate K’ for each pipe
Calc. K’ for each pipe
K’=(0.0252)fL/D5
For simplicity f is usually assumed to be the same (typical value is .02) in all parts of the network

## Slide 12: 5. Assume flow rates and directions
Requires assumptions the first time around
Must make sure that Qin=Qout at each node

## Slide 13: 6. Calculate Qt-Qa for each independent loop
Qt-Qa =-∑K’Qan/n ∑ |Qan-1|
n=2 (if Darcy-Weisbach is used)
Qt-Qa =-∑K’Qa2/2 ∑ |Qan-1|
Qt is true flow
Qa is assumed flow
Once the difference is zero, the problem is completed

## Slide 14: 7. Apply Qt-Qa to each pipe
Use sign convention of step one
Qt-Qa (which can be + or -) is added to CW flows and subtracted from CCW flows
If a pipe is common to two loops, two Qt-Qa corrections are added to the pipe

## Slide 15: 8. Return to step 6
Iterate until Qt-Qa = 0

## Slide 16: Example Problem
2 loops; 6 pipes
  By hand; 1 iteration
  By spreadsheet

## Slide 17: Hardy-Cross Example 1

## Slide 18: Hardy Cross Ex 2

## Slide 19: Hardy Cross-Solve using Excel

## Slide 20: Next Lecture
Equivalent Pipes
Pump Performance Curves
System Curves