## Slide 1: CTC 450 Review
Distributing flow in a pipe network
  Hardy-Cross Method
    At any node: Flows in = flows out
    Head losses around a loop = 0
Equivalent Pipes (parallel/series)
Pump (performance and system curves)

## Slide 2: Objectives
Manning’s Equation-Open Channel Flow
Rational Method

## Slide 3: Uniform Flow in Open Channels
Water depth, flow area, Q and V distribution at all sections throughout the entire channel reach remains unchanged
The EGL, HGL and channel bottom lines are parallel to each other
No acceleration or deceleration

## Slide 4: Manning’s Equation
Irish Engineer
“On the Flow of Water in Open Channels and Pipes” 1891
(“On the Origin of Species”-1859)
Empirical equation
See more on history:
  http://manning.sdsu.edu/\
  http://el.erdc.usace.army.mil/elpubs/pdf/sr10.pdf#search=%22manning%20irish%20engineer%22

## Slide 5: Manning’s Equation-Metric
Q=AV=(1/n)(A)(Rh)2/3S1/2
Where:
Q=flow rate (cms)
A=wetted cross-sectional area (m2)
Rh=Hydraulic Radius=A/WP (m)
WP=Wetted Perimeter (m)
S=slope (m/m)
n=friction coefficient (dimensionless)

## Slide 6: Manning’s Equation-English
Q=AV=(1.486/n)(A)(Rh)2/3S1/2
Where:
Q=flow rate (cfs)
A=wetted cross-sectional area (ft2)
Rh=hydraulic radius=A/WP (ft)
WP=wetted perimeter (ft)
S=slope (ft/ft)
n=friction coefficient (dimensionless)

## Slide 7: Manning’s Equation-Solve for Q or Velocity
Can also divide both sides by area and write the equation to solve for velocity

## Slide 8: Manning’s Equation-Velocity-Metric
V=(1/n)(Rh)2/3S1/2
Where:
V=velocity (meters/sec)
Rh=Hydraulic Radius=A/WP (m)
WP=Wetter Perimeter (m)
S=slope (m/m)
n=friction coefficient (dimensionless)

## Slide 9: Manning’s Equation-Velocity-English
V=(1.486/n)(Rh)2/3S1/2
Where:
V=velocity (feet per second)
Rh=hydraulic radius=A/WP (ft)
WP=wetted perimeter (ft)
S=slope (ft/ft)
n=friction coefficient (dimensionless)

## Slide 10: Manning’s Friction Coefficient
http://www.lmnoeng.com/manningn.htm
Typical values:
  Concrete pipe: n=.013
  CMP pipe: n=.024

## Slide 11: Example-Find Q
Find the discharge of a rectangular channel 5’ wide w/ a 5% grade, flowing 1’ deep. The channel has a stone and weed bank (n=.035).
A=5 sf; WP=7’; Rh=0.714 ft
S=.05
Q=38 cfs

## Slide 12: Example-Find S
A 3-m wide rectangular irrigation channel carries a discharge of 25.3 cms @ a uniform depth of 1.2m. Determine the slope of the channel if Manning’s n=.022
A=3.6 sm; WP=5.4m; Rh=0.667m
S=.041=4.1%

## Slide 13: Friction loss
How would you use Manning’s equation to estimate friction loss?
Find slope and multiply by length

## Slide 14: Triangular/Trapezoidal Channels
Must use geometry to determine area and wetted perimeters

## Slide 15: Pipe Flow
Hydraulic radii and wetted perimeters are easy to calculate if the pipe is flowing full or half-full
If pipe flow is at some other depth, then tables are usually used

## Slide 16: Historic SCS data for channels

## Slide 17: Using Manning’s equation to estimate pipe size
Size pipe for Q=39 cfs
Assume full flow
Assume concrete pipe on a 2% grade
Put Rh and A in terms of Dia.
Solve for D=2.15 ft = 25.8”
Choose a 27” or 30” RCP

## Slide 18: Project 3 (Flowmaster)

## Slide 19: Rational Formula
Used to estimate peak flows
Empirical equation
For drainage areas<200 acres
Other methods:
  TR-55 (up to 2,000 acres)
  TR-20
  Regression Models

## Slide 20: Peak Runoff Variables
Drainage area
Infiltration
Time of Concentration
Land Slope
Rainfall Intensity
Storage (swamps, ponds)

## Slide 21: Rational Method
Q=CIA
Q is flowrate (cfs)
C is rational coefficient (dimensionless)
I is rainfall intensity (in/hr)
A is drainage area (acres)
Note: Units work because 1 acre-inch/hr = 1 cfs

## Slide 22: Derivision
Assume a storm duration = time of conc.
Volume of runoff assuming no infiltration
= avg. intensity*drainage area*storm duration
=I*A*Tc

## Slide 23: Theoretical runoff hydrograph
Area under hydrograph = ½ *2Tc*Qp=Tc*Qp

## Slide 24: Derivision of Rational Method
Volume of rain = Volume observed as Runoff
I*A*Tc=Tc*Qp
Qp=IA
To account for infiltration, evaporation, and storage add a coefficient C (C<1)
Qp=CIA

## Slide 25: Rational Coefficient C
Don’t confuse w/ Manning’s coefficients
Typical values:
  Pavement 0.9
  Lawns 0.3
  Forest 0.2
  There are also many detailed tables available

## Slide 26: Weighted Rational Coefficient C
Must be weighted if you have different area types within the drainage area
Drainage area = 8 acres:
2 acres; C=0.35 (residential suburban)
6 acres; C=0.2 (undeveloped-unimproved)
Weighted C=[(2)(.35)+(6)(.2)]/8 = 0.24

## Slide 27: Time of Concentration
Time required for water to flow from the most distant part of a drainage area to the drainage structure
Sheet flow
Shallow, concentrated Flow
Open Channel Flow

## Slide 28: IDF Curve
Shows the relationship between rainfall intensity, storm duration, and storm frequency.
IDF curves are dependent on the geographical area
Set time of concentration = storm duration

## Slide 29: IDF Curve (SUNY Poly)
SUNY Poly Campus

## Slide 30: MA7CD10 Definitions (7Q10)
Minimum Average seven-consecutive-day low flow with a ten year return frequency
The lowest stream flow for seven consecutive days that would be expected to occur once in ten years.
The period of lowest stream flow during a seven-day interval that is expected to occur once every 10 years

## Slide 31: 7Q10 Importance
WW treatment plants usually discharge to nearby rivers
7Q10 is considered a low-flow value (least dilution capacity)

## Slide 32: Determining 7Q10
See your book page 64:
Streamflow data (lowest 7-day avg flow)
Calculate probability
Graph data on logarithmic probability paper (find line of best fit)
Extrapolate line to 90% (probability of larger flow) and determine 7Q10

## Slide 33: Next Lecture
Water Quality
Water Distribution Systems