## Slide 1: CTC 450
Pumps
http://www.esi-group.com/SimulationSoftware/CFD_ACE/blood.html

## Slide 2: Objectives
Ability to simplify pipe systems by use of equivalent pipes (parallel and series)
Know what types of pumps are available
Ability to develop a pump performance curve
Ability to develop a simple system curve

## Slide 3: Equivalent Pipes
An imaginary conduit that replaces a section of a real system such that the head losses are identical for the quantity of flow
Note: Use Chapter 2, page 34 (Figure 2-15) to solve Ch 7 (#15) Homework

## Slide 4: Equivalent Pipe to Replace Parallel Pipes
Determine an equivalent pipe 1000’ in length to replace two parallel pipes (8” pipe @ 1000’ and 6” pipe @ 800’)
Assume a head loss (10’) and calculate HGL slopes of both pipes (10’/1000’) and (10’/800’). Using diameters and HGL slopes calculate Q in both pipes from Hazen-Williams nomograph (550 & 290 gpm)
Total Q’s (840 gpm)
Use nomograph w/ HGL slope (10’/1000’) and total Q to get equivalent pipe size (answer=9.4”)

## Slide 5: Equivalent Pipe to Replace Serial Pipes
Determine an equivalent pipe 2000’ in length to replace three pipes in series (8” pipe @ 400’ , 9.4” pipe @ 1,000’ and 10” pipe @ 600’)
Assume a flow (500 gpm) and calculate head losses in all 3 pipes from Hazen-Williams equation or nomograph (3.3+3.8+1.6=8.7’ per 2000’)
Determine head losses per 1000’ (4.4’ per 1,000 ft)
Use nomograph w/ calculated head loss and assumed Q to get equivalent pipe size (answer=9.2”)

## Slide 6: Pumps
Machines that do work on fluids
Pumps increase the pressure in a pipe, or lift water, or move water
  Axial-flow
    Flow is parallel to axis
    Best suited for low heads and high flows
  Radial-flow (centrifugal)
    Flow is perpendicular to axis
    Best suited for high heads

## Slide 7: Pump Performance Curves
Obtained by experimental data and plotted on graphs (usually for a specific pump at a specific rotation speed)
  Head versus discharge
  Efficiency versus discharge
  Shutoff head is the pressure head if discharge is completely stopped (Q=0)

## Slide 8: Pump Efficiency
Efficiency is defined as the motor power input divided by the power output
Centrifugal pump efficiency is usually in the range of 60-85%
Axial pump efficiency is usually in the range of 75-92% (highly efficient in high-flow, low-lift conditions)

## Slide 9: Pump Curve (1750 rpm)

## Slide 10: Variable Speed Pumps
Pumps which can be operated at variable speeds
Have 2 pump curves (high speed and low speed) and pump can operate between the curves

## Slide 11: System Head Curves accounts for static head and friction losses
Static head (lifting of water to a higher elevation)
Friction losses (increases as the flow increases)
In real systems, outputs are variable and the system head “curve” is actually a “band”
Pump should be operated at the intersection of the system-head curve and the head-discharge curve

## Slide 12: System Head Curve Example
Curve 1 – Pump is used to “raise” water from a lower source to a higher tank (outlet 1)
Curve 2 – Pump is used to raise water to a load center (outlet 2)
Actual operation can vary between the curves depending on how much flow is discharging from outlet 1 and 2

## Slide 13: System Curve-Simple Example

## Slide 14: System Curves Curve 1: Pump to Storage Curve 2: Pump to Load
What do H1 and H2 represent?
How do you calculate the increase in head based on the pumping rate?
Answer: Use Hazen Williams (Vary Q for C and D; find slope)

## Slide 15: Pump & System Head Curves Example
Pump operates at A when pumping only to storage
Pump operates at B when pumping only to the load
Pump operates at C when pumping partly to the storage tank and partly to the load

## Slide 16: Example-Discussion of Pumps Small Systems
Small system
  Use 2 constant speed pumps with same capacity
  Intermittently pump to tank
  Control by fluctuation of water level in tank
  Elevated storage maintains pressure in the system

## Slide 17: Example-Discussion of Pumps Large System
Large system
  Use 3 pumps in parallel (1 as standby)
  Operate pumps individually or in combination to meet demand

## Slide 18: Example Pump Curve-Armstrong
http://www.armstrongpumps.com/present_newsletter.asp?groupid=1&nlfile=00_00_054

## Slide 19: Example Pump Curve-Taco

## Slide 20: Example Pump Curve-Goulds

## Slide 21: Pump Operation Scenarios Single Pump
Constant speed (as flows change the pump pressure changes)
Variable speed (maintains a constant pressure over a wide range of flows by varying the rotational speed of the pump impellor)

## Slide 22: Pump Operation Scenarios Multiple Pumps
Multiple pumps – parallel – one as “standby”
Multiple pumps – series – to increase discharge head

## Slide 23: Pump Simulation
http://www.simerics.com/simulation_gallery.html

## Slide 24: WW/Solids Handling Apps

## Slide 25: Next Lecture
Manning’s Equation (open channel flow)
Rational Method

## Slide 26: Pump Trivia
A pumping condition where the water level is below the eye of the impellor---suction lift condition.
A pumping condition where the water level is higher than the impellor--- suction head condition.