## Slide 1: CTC 450 Review
WW Sludge Processes

## Slide 2: Objectives
Understand the basics with respect to operation of wastewater systems

## Slide 3: Manage Life Cycle
Design
Construction
Startup
Operation
Maintenance
Repair
Replace
Don’t “run to fail”

## Slide 4: Two systems
Treatment plant (small footprint)
Sewer collection system (large footprint)

## Slide 5: Legislation for Discharge
NPDES-National Pollution Discharge Elimination System (SPDES)
Set up to reduce frequency and occurrence of sewer overflows and to notify public when overflows occur
EPA estimates 23,000-75,000 sanitary overflows annually

## Slide 6: Capacity of WW Treatment
Evaluate overall performance of plant
Evaluate performance of individual processes within a plant

## Slide 7: Plant Performance
Regulatory inspections
  Ensures self-monitoring is implemented
  Influent plant hydraulics
  Influent plant organic loadings
  Quality of effluent wastewater
  Property of sludge solids
  Common tests (BOD/SS/pH)
    Others-coliform/chlorine residual/phosphorus, ammonium nitrogen/presence of heavy metals

## Slide 8: Individual Process Performance (1/3)
Primary Sedimentation
  Flow
  BOD and SS of influent/effluent
  Volume of sludge withdrawn
  Sludge total solids content
Example-Poor sludge thickening
  Hydraulic overload (not enough time to settle)
  Poor operating procedure (pumping sludge at such a high rate that the water above the sludge layer is pumped out)

## Slide 9: Individual Process Performance (2/3)
Secondary Treatment
  BOD and SS of influent/effluent
  Volume of sludge withdrawn
  Sludge total solids content
Processes which can be tweaked
  Air supply
  Recirculation rate
  Rate of sludge wasting
  Optimize performance of activated sludge systems by measuring and varying DO, MLSS and F/M ratios

## Slide 10: Individual Process Performance (3/3)
Sludge handling
  Estimate solids capture
  Don’t recycle fine solids (by recycling WW through processes that can never remove those fines---can avoid by increasing chemical conditioning when dewatering sludge)

## Slide 11: Estimating Solids Capture
The performance of a centrifuge dewatering anaerobically digested sludge was evaluated to determine the capture of SS. Samples were tested as follows:
Ss (total solids-incoming sludge)
  35,000 mg/l (3.5%)
Sc (total solids in cake)
  280,000 mg/l (28%)
Sf (SS in centrate/filtrate)
  1,200 mg/l (0.12%)

## Slide 12: Solids Capture-Equation
Qs=Qf+Qc
Ms=Mf+Mc
Mass(M)=Concentration(S)*Flow(Q)
% Solids Removal=Mc/Ms (also see next slide)
% Solids Remaining=Mf/Ms
s-incoming liquid sludge
f-outgoing filtrate (centrate)
c-outgoing cake
Qs,Ss,Ms
Qc,Sc,Mc
Qf,Sf,Mf

## Slide 13: Proof of Equation Mc/Ms
PROOF
Equation 12-4

## Slide 14: From previous slide
Fraction of solids removed (Mc/Ms)=
[Sc*(Ss-Sf)] / [Ss*(Sc-Sf)] =
97% Removal

## Slide 15: Take-Home Worksheet
Answer: 46% solids removal

## Slide 16: Capacity of Sewer Collection
Infiltration/Inflow Surveys
Inspection via cameras
Regulation of Sewer Use
Sewer Charges and Revenues

## Slide 17: Extraneous Inflow
Sewer surcharging results in
  Overloading of plant
  Overtaxing pumping stations
  Costs of treating excess ww
  Health hazards if untreated ww is discharged to receiving water
Historically, peaks were bypassed around the treatment plant
Current goal is to handle peaks

## Slide 18: Infiltration/Inflow
Infiltration from groundwater
  Overloading of plant
  Overtaxing pumping stations
  Increased costs of treating excess ww
  Health hazards if untreated ww is discharged to receiving water
Inflow-direct connections such as roof drains

## Slide 19: Reducing Peaking Problems
Evaluate magnitude of the problem
Rehabilitate existing sewer system
Extend treatment facilities

## Slide 20: Video Inspection
Used to detect structural soundness
  Service connections not plugged when no longer needed
  Cross-connections with storm systems
  Unauthorized drainage connections
  Tree roots
  Structural damage

## Slide 21: Regulation of Sewer Use
Goals
  Control discharges to the system
    No septic tanks
    Unpolluted waters to storm system
  Ensure water quality standards
    No hazardous wastes
  Equitable customer charges
    Flow measuring and sampling station for industrial users

## Slide 22: Sewer Charges
Payment should be in proportion to use and benefits received
Payment often based on flow quantities with surcharges for wastewater strength

## Slide 23: Service Charge
Calculate the service charge for a dairy wastewater based on the following info:
Daily flow = 150,000 gpd
Avg BOD=910 mg/l
Avg SS= 320 mg/l
Service Charge=$450 per million gallons
Surcharge of 2.38 cents per lb of excess BOD (BOD>250 mg/l)
Surcharge of 1.83 cents per lb of excess SS (SS>300 mg/l)

## Slide 24: Service Charge Example 12-3
Service charge for flow = $67.50/day
  $450/mg*0.15 mg/day
Service charge for excess BOD = $19.65/day
  (910-250)/1E6*150,000gpd*8.34*/gal*0.0238/lb
Service charge for excess SS = $0.46/day
  (320-300)/1E6*150,000gpd*8.34*/gal*0.0183/lb
Total Charge = $87.61/day

## Slide 25: Management Structure
Utility info
Maintenance
Operators
Computer maintenance
SCADA systems

## Slide 26: Additional Documents
Oneida County Sewer District Map
Water Pollution Control Plant and Sauquoit Creek Pump Station Evaluation
Note: These documents can be found on Brightspace