## Slide 1: CTC 450 Review
WW Collection Systems
  Sewage vs Storm Systems
  Types of pipes
  Installation

## Slide 2: Objectives
Understand basic processes for treating wastewater

## Slide 3: Designing Against Disease
Designing Against Disease
http://www.tbp.org/pubs/Features/W10Bell.pdf
Who graduated at age 15 from Dartmouth Thayer’s School of Engineering?
Allen Hazen (1869-1930)
Slow sand filtration clarifies water. What else does it do?
Removes 99% of bacteria
What two design qualities are used to determine a material for filtration?
Effective size and uniformity coefficient
What percentage of the population in Chicago probably contracted typhoid in 1890-1892?
5%
Who is considered the father of sanitary engineering in America?
Hiram Mills (1836-1921)

## Slide 4: WW Treatment
Combination of physical and biological processes
Processes are used to remove organics and solids (reduce BOD and SS)

## Slide 5: History of Developing Processes
Imhoff tanks used originally for settling of solids
Treatment of water through gravel bed (1910)
Activated sludge (1920s)
RBC’s (1959-Germany)

## Slide 6: Imhoff Tank
The Imhoff tank obtained its name from its inventor, Dr. Karl Imhoff of Germany. It is a variation of the septic tank in which two chambers are provided, one above the other. The upper sedimentation or flow chamber is for settling solids and the lower chamber is for anaerobic digestion of sludge. Solids settle to the bottom of the flow chamber passing through a slot at the bottom into the lower chamber. The slot is baffled in such a manner that gas rising from the lower chamber does not interfere with the sedimentation process in the upper chamber. A gas vent, known as the scum chamber, extends from the lower compartment up to the tank surface between the outside wall of the sedimentation chamber and the Imhoff tank enclosing wall. The main advantage of this type of tank over the septic tank is that sludge is separated from the effluent, which allows for more complete settling and digestion. Operated properly, these systems are capable of removing 30 to 60 percent of the suspended matter, and from 25 to 40 percent of the BOD. www.vnh.org/ PreventiveMedicine/Chapter7/7.08.html

## Slide 7: Trickling Filter

## Slide 8: Activated Sludge (Aeration Tank
http://www.steve.gb.com/science/biotransformation.html

## Slide 9: Rotating Biological Contactor
http://www.dmw.co.jp/english/temp/enban/enban-kata.html

## Slide 10: Basic Processes-Municipal
Primary Treatment
  Grit chamber
  Primary Settling
Secondary Treatment
  Biological Treatment
  Final Settling
Disinfection
  Contact Basin

## Slide 11: Aeration Tank

## Slide 12: Basic Processes-Small
Aeration, Settling, Disinfection (no primary treatment)
Series of Stabilization Ponds

## Slide 13: Solids Treatment
Solids are generated from primary settling and final settling
Solids are usually treated via sludge digesters

## Slide 14: Typical Effluent Quality Standards
BOD and SS Max. monthly avg of < 30 mg/l (<.003% solids)
pH between 6 and 9
Oil and grease < 10 mg/l

## Slide 15: Design Loading
Load (#’s of BOD or SS)
Flow (flow rates)
Peak hourly flow, maximum monthly flow, annual average, average dry weather, average wet weather

## Slide 16: Design Criteria for Various Treatment Processes
 | Peak Hourly Flow | Max. Monthly Flow | Other
Flow measurement | X |  | 
Bar Screen | X |  | 
Pumps | X |  | Min Hourly Flow
Grit Chamber | X | X | 
Primary Settling |  | X | 
Final Settling |  | X | 
Disenfection | X |  | 

## Slide 17: Preliminary Treatment
Flow is measured (Parshall flume)
Screening (1/2” or 1” spacing)
  (with grinder or shredder-¼” size)
Grit Chamber (sand; coffee grounds)

## Slide 18: Parshall Flume
A Parshall flume is a specially shaped structure which can be installed in a channel to measure the water flow rate. The flume was developed and calibrated by Ralph Parshall at Colorado State University early in this century and has been used extensively. Although Parshall flumes are difficult devices to set and build, they are an accepted and widely used measuring device. waterknowledge.colostate.edu/ parshall.htm

## Slide 19: Plan and Profile-Parshall Flume
web.deu.edu.tr/atiksu/ toprak/ani4022.html

## Slide 20: Automated Bar Screen

## Slide 21: Grinders

## Slide 22: Grit Chamber

## Slide 23: Other Ways to remove grit
Removal in primary clarifier
Aerated units w/ hopper bottoms
Forced vortex tanks (proprietary)

## Slide 24: Grit Removal Trivia
The recommended velocity of a properly operated grit removal system is 1 foot per second.
This velocity allows the grit to settle but the majority of the organics to remain suspended.

## Slide 25: Clarifiers (settling/sedimentation tanks)
Primary (before biological treatment)
Intermediate (in between biological treatments)
Final (following biological treatment)

## Slide 26: Primary Clarifier Schematic

## Slide 27: Primary Clarifiers-Shapes
www.cityofweirton.com/ wsb/treatment.htm
www.nwlink.com

## Slide 28: Primary Clarifier-Construction

## Slide 29: Clarifier-Rendered Image and Parts

## Slide 30: Design Criteria for Primary Clarifiers
See my website-bottom of 450 schedule)
  Overflow rates
  Side water depth
  Weir loading
  Notes: Includes EPA standards and “Standards” based on a report of the WW Committee of the Great Lakes
  Note: Secondary solids --- activated sludge solids are returned to the primary for removal with primary solids

## Slide 31: Primary Clarifier Example

## Slide 32: Description
Two primary settling tanks are 95 ft in diameter w/ a 7’ side water depth. Single effluent weirs are located on the peripheries of the tanks. For an average design flow of 10.0 mgd and peak flow of 15.4 mgd calculate the overflow rate, detention time and weir loading

## Slide 33: Calculate Overflow rate
Surface area of 2 tanks = 14,200 ft2
Volume (7’) depth=99,400 ft3 =0.744 million gal.
Overflow rate=Q/A=704 gpd/ft2(avg design flow)
Overflow rate=1084 gpd/ft2 (peak flow)
Check that values are less than design stds (average)---Okay
  Average EPA 800-1200 gpd/square ft
  Average “Great Lakes” Standards 1000 gpd/square ft
Check that values are less than design stds (peak)----Okay
  Peak EPA 2000-3000 gpd/square ft
  Average “Great Lakes” Standards 1500 gpd/square ft
33

## Slide 34: Calculate Detention Time
Vol/Q=(0.744E6 gallons/10 mgd)*24 hr/day
=1.8 hours (average design flow)
Note: Can also use H/Vo (depth of water/overflow rate—but remembering V/Q is easier for me)
34

## Slide 35: Calculate Weir Loading
Weir length for 2 tanks = 2*pi*D=2*pi*95 ft=597 ft
Weir loading = Q/weir length= 10E6 gpd/597 ft
=16,750 gpd/ft (check standards---see below)
Okay per EPA standards (10,000-40,000 gpd/ft) but not for “Great Lake” standards (10,000 gpd/ft)
Could add a 2nd set of weirs to get to 8,400 gpd/ft
35

## Slide 36: Check Side Water Depth
Side Water Depth = 7’
Not okay per EPA standards (10-13 ft)
Okay per “Water Works” standards (7’)
36

## Slide 37: Intermediate Clarifier
Sometimes used for 2-stage secondary treatment processes:
  Between 2 trickling filters
  Between trickling filter and activated sludge
Typical Values:
  Overflow rate 600-800 gpd/sq ft
  Minimum water depth should be 10 ft
  Weir loading:
    10,000 to 20,000 gpd/linear ft
37

## Slide 38: Final or Secondary Clarifiers
There are differences in sludge characteristics between trickling filters and activated sludge:
Design of final clarifiers following trickling filters is similar to design of primary clarifiers
Design of clarifiers following activated sludge systems must take into account the reduced settleability.
  Deeper
  Lower overflow rate
  Longer weir length

## Slide 39: Final Clarifiers-After TF vs After AS
Settles Readily
Less buoyant
Depth – a few inches
Sludge is removed less frequently
Tank not as deep
Hard to Settle
Lighter, more buoyant
Depth – 1 to 2 feet
Rapid, uniform sludge withdrawal is ideal
Tank is usually deeper

## Slide 40: Final (Secondary) Clarifier Example

## Slide 41: Description
Determine the recommended size of two new circular secondary clarifiers for an activated sludge system w/ a design flow of 20,000 m3/day with a peak hourly flow of 32,000 m3/day. Use maximum overflow rates of 33 m3/m2-day at design monthly flow and 66 m3/m2-day at peak hourly flow.
41

## Slide 42: Calculate Required Surface Area & Tank Diameter
Design Monthly Flow
Required Surface area = Design flow Rate/Maximum Overflow Rate
=20,000/2*33=303 square meters
Assuming 2 tanks, calculate the diameter=19.6 meters
42

## Slide 43: Check Peak Overflow Rate
Peak Flow
Required Surface area = Peak flow Rate/Maximum Overflow Rate
=32,000/2*66=242 square meters
Assuming 2 tanks, calculate the diameter=17.6 meters
Use worst case: Diameter must be 19.6 meters
43

## Slide 44: Example 11-2 Check Weir Loading
Assuming the inboard weir channel is set on a diameter of 20 meters
Weir loading=Q/weir length
=32,000/(pi*19.6 m*2 tanks)=260 m3/m2-day
(Maximum is 125 to 250; design is just over maximum)
44

## Slide 45: Side Water Depth
The recommended side water depth for a tank diameter between 50 and 100 feet is 11 ft (reference was prior book)
45

## Slide 46: Review Question
What are two types of solids effectively removed by primary clarifiers?
A. Floatable and settleable
B. Floatable and dissolved
C. Dissolved and colloidal
D. Suspended and organic
46

## Slide 47: Review Questions
What are the differences between a primary, intermediate and final clarifier?
What can be used to measure the incoming flow rate?
47