## Slide 1: CTC 450 Review
Water Quality (SPDES/SWPPP/NOI)
Water Distribution Systems

## Slide 2: Objectives
Describe the basic processes for treating groundwater and surface water
Calculate chemical coagulation detention times for both completely mixed and plug-flow reactors

## Slide 3: Water Treatment Objective
Provide water that is chemically and microbiologically safe for human consumption.
  Domestic Use (free from apparent turbidity, color, odor or objectionable taste)
  Industrial Use (may be more stringent; decrease hardness to prevent scale deposits)

## Slide 4: Primary Processes
Presedimentation
Chemical clarification (coagulation, sedimentation and filtration)
Precipitation Softening
Disinfection
Fluoridation
Chlorination

## Slide 5: Processing Requirements
Groundwater from wells is usually easily processed (may only need disinfection and fluoridation)
River water usually requires the most processing (much variation)
Water from lakes/reservoirs is usually in-between

## Slide 6: Current Standards
  Homework/Tests: Given configurations and flow data calculate existing parameters and compare to standards provided for this class.
  2022-Current
  Archived (2012/2007/1990/1980)
  Ref: https://www.health.state.mn.us/communities/environment/water/tenstates/standards.html
  Note: for this class use standards found here- https://people.sunypoly.edu/~barans/classes/ctc450/pdf/CTC%20450%20W_WW%20Standards.docx.pdf

## Slide 7: Presedimentation
Used to settle out heavy solids from muddy river water prior to chemical flocculation/sedimentation.
Detention time should be greater than or equal to 3 hours.

## Slide 8: Mixing and Flocculation Sedimentation
Rapid mixing of chemicals with raw water
Flocculation
Sedimentation (settling tank)

## Slide 9: Water Treatment Process

## Slide 10: Water Works Standards Rapid Mixing
  Detention time for rapid mixing<30 seconds

## Slide 11: Water Works Standards Flocculation
  Design inlets/outlets to prevent short-circuiting and floc destruction
  Detention time for floc formation >=30 minutes
  Flow-through velocity shall be 0.5 to 1.5 ft/min
  Flocculation/sedimentation basins shall be as close together as possible
  Reduce turbulence at bends and changes in direction

## Slide 12: Sedimentation
Removal of particulates, chemical floc and precipitates through gravity settling
Most are designed as upflow clarifiers where water rises vertically and solids settle to tank bottom where they are removed mechanically
Water enters the bottom and exits the top through a weir

## Slide 13: Water Works Standards Sedimentation
  Detention time >=4 hours
  Max. horizontal velocity is 0.5 ft/min
  Max weir loading is 20,000 gpd/ft of weir length
  Overflow rate in range of 500-800 gpd/sq ft
  Overflow rate (upflow velocity)

## Slide 14: Reaction Rates
Zero-order: Rate of reaction is not dependent on concentration
First-order: Rate is dependent upon concentration of the reactant (the higher the concentration the faster the rate).
First-order is most common in W&WW processes

## Slide 15: Zero Order
C=Co-k*t (y-intercept=?) (slope=?)
Where:
C=Concentration of a reactant at any time t (mg/l)
Co=Initial concentration of reactant (mg/l)
k=Reaction-rate constant (per day)
t=Elapsed time (days)

## Slide 16: First Order
C=Coe-kt
Where:
C=Concentration of a reactant at any time t (mg/l)
Co=Initial concentration of reactant (mg/l)
k=Reaction-rate constant (per day)
t=Elapsed time (days)

## Slide 17: Detention Time Completely Mixed; First Order
t=(1/k)*((Co/Ct)-1)
t=time
k=rate constant (ideally obtained by lab experiments)
Co=initial concentration
Ct=concentration @ time t
Note: t and k must have consistent units

## Slide 18: Detention Time Plug Flow; First Order
t=(1/k)*(ln of Co/Ct)
Where t=time
k=rate constant
Co=initial concentration
Ct=concentration @ time t
Note: t and k must have consistent units

## Slide 19: Detention Times
Problem Statement: Based on lab studies, the rate constant for a chemical coagulation reaction was found to be first-order kinetics with a k equal to 75 per day. Calculate detention times required for completely mixed and plug flow reactors for an 80% reduction. Given
Co=200 mg/l then Ct=? (40 mg/l for 80% reduction)

## Slide 20: Detention Time-Completely Mixed
20
t=(1/k)*(Co/Ct-1)
t=(day/75*1440 minutes/day)*(200/40-1)
t=77 min
Note: the detention time (Vol/Q) must be at least 77 minutes to obtain an 80% reduction in concentration
Notes: 20

## Slide 21: Detention Times-Plug Flow
21
t=(1/k)*(ln of Co/Ct)
t=(1440/75)*(ln of 200/40)
t=31 min
Note: the detention time (Vol/Q) must be at least 31 minutes to obtain an 80% reduction in concentration
Notes: 21

## Slide 22: Sedimentation Tank
22
Each half of an in-line treatment plant has the following sized units:
Rapid Mixing Chamber: 855 ft3
Flocculation Tank: 140’ wide; 58’ long; 14.5’ liquid depth
Sedimentation Tank: 140’ wide; 280’ long; 17’ liquid depth
Weir Length: 1,260’
Design Flow: 40 mgd (assume 40 mgd per half of in-line treatment); Total flow to plant would be 80 mgd
Compare values to waterworks standards
Notes: 22

## Slide 23: Sedimentation (Check Detention Times)
23
Calculate other flow units given 40mgd:
  27,800 gpm
  5,348,000 cubic ft/day
  3,710 cubic ft/minute
Determine Rapid Mixing Detention Time
  V/Q=855/3710*60=14 seconds (Std<30 seconds; okay)
Determine Floc Tank Detention Time
  V/Q=[(140*58*14.5)]/3710=32 minutes (Std>30 minutes; okay)
Determine Sed Tank Detention Time
  V/Q=[(140*280*17)]/3710=180 min=3 hr (Std>4 hours; not okay)
Notes: 23

## Slide 24: Sedimentation (check other standards)
Check Sed Tank Horizontal Velocity:
  V=Q/A=3710/(140*17)=1.6 ft/min (Std<0.5 ft/min; not okay)
Check Weir Loading
  Q/L=40 mgd/1260 ft=32,000 gpd/ft (Std<20,000 gpd/ft; not okay)
Check overflow rate
  Q/surface area= 40 mgd/(140*280’)=1020 gpd/sq ft (Std 500-800 gpd/sq ft; not okay)

## Slide 25: Ballasted Flocculation
Ballast (heavy substance-microsand) is used to enhance flocculation and sedimentation.
ACTIFLO(trademark)---polymer/microsand is added which reduces floc/settling times by a factor of 6 or more.
Example Project in Colorado using Ballasted Flocculation/Sedimentation (skip 1st/last page)

## Slide 26: Water Purification Facility 1/2

## Slide 27: Water Purification Facility 2/2

## Slide 28: Flocculator-Clarifiers
Also known as solids contact units
Combines mixing, flocculation and sedimentation in a single tank
Advantages are less footprint and less cost
Disadvantage is less operating flexibility

## Slide 29: Filtration
Removes nonsettleable solids
Usually consists of graded gravel and filter media (sand and anthracite)
Backwashing is used to clean the filter (mechanical or air agitation may also be used)

## Slide 30: Filtration Media
Complex reactions including straining, flocculation and sedimentation
Best to use the entire filter depth (not just the top few inches, which clogs the filter quickly)

## Slide 31: Filter Underdrain
Pipe laterals with orifices or nozzles
Vitrified tile block
Plastic dual-lateral block
Plastic nozzles

## Slide 32: Other Filter Types
Diatomaceous earth (small application)
Microstrainers
Slow sand filters

## Slide 33: Filtration Example
A filter unit is 15 ft by 30 ft. After filtering 2.50-million gallons in a 24-hr period, the filter is backwashed at a rate of 15 gpm/square ft for 12 minutes.
Compute the average filtration rate and the quantity and percentage of treated water used in backwashing.

## Slide 34: Filtration Example Answers
Surface Area of filter unit = 450 ft2
Filtration rate= Q/A= 3.9 gpm/ft2
Quantity of wash water=15gpm/ft2 *12 min*450 = 81,000 gal
Wash water/treated water= 81,000/2.5E^6 = 3.2%

## Slide 35: Chemical Feeders
Applies chemicals at a constant rate
Liquid or dry
Apply a specific volume or a specific weight
Volumetric dry feeders are simpler but a little less accurate

## Slide 36: Coagulants
Most common is alum (aluminum sulfate)
Less common are other aluminum-based coagulants and those based on iron
Synthetic polymers are sometimes used to aid coagulation

## Slide 37: Taste & Odor Control
Specific to each site
Aeration
Carbon adsorption
Potassium permanganate
Manganese zeolite process
Water softening

## Slide 38: Precipitation Softening
Hardness in water is caused by Ca and Mg ions
Softening uses lime and soda ash
Split treatment is sometimes used to avoid wasting lime

## Slide 39: Avoid Corrosion by:
using cement mortar inside of pipe
forming a protective film of calcium carbonate
cathodic protection

## Slide 40: Waste Streams
Sludge from the settling tank (after chemical coagulation or softening processes)
Wash water from backwashing filters
Treatments
  Pipe to municipal sewer
  Discharge to lagoon
  Process for disposal to landfill