## Slide 1: CTC 450 Review
Water processing
Add coagulator (alum), settle, filter

## Slide 2: Objectives
Understand the following processes:
  Fluoridation and defluoridation
  Chlorination
  Disinfection
Know the waste streams generated by water treatment processes and how the waste streams are treated

## Slide 3: Fluoridation
Too little fluoride increases incidence of cavities
Too much fluoride can cause mottling of teeth (>2--4 mg/l)
Optimum fluoride reduces incidence of cavities (0.6 to 1.2 mg/l)
http://mybrownstonedental.com/tooth-fillings-houston-dentist/cavity
http://fluoridealert.org/issues/fluorosis/

## Slide 4: Fluoride References
Fluoride Paper (in Blackboard)
Database: water supply fluoridation
https://nccd.cdc.gov/DOH_MWF/Default/Default.aspx

## Slide 5: Fluoride
Add fluoride using sodium fluoride, sodium silicofluoride or fluorosilicic acid
Remove fluoride by activated alumina or bone char

## Slide 6: Chlorination
Used for disinfection, oxidation and for providing a residual disinfection
Chemical reactions are complex and depend on pH, temperature, time and ammonia concentration

## Slide 7: Chlorine
Heavier than air
Greenish-yellow-colored toxic gas
Strong oxidizer
Extremely corrosive
Respiratory irritant

## Slide 8: Chlorine as Disinfectant
Chlorine combines w/ water to form hypochlorous acid (HOCl) which can then ionize to the hypochlorite ion H+ & OCl- when the PH>8
Chlorine combines with ammonia to form combined residuals
Adding additional chlorine results in free residual

## Slide 9: Chlorine-Ammonia Products
Monochloramine (NH2Cl)
  Forms in pH range of 4.5 to 8.5
  Monochloramine exists alone when pH > 8.5
Dichloramine (NHCl2)
  Forms in pH range of 4.5 to 8.5
Trichloramine (NCl3)
  Forms when pH < 4.4

## Slide 10: Chlorination Curve
Chlorine first reacts w/ reducing agents (nitrites, ferrous iron and hydrogen sulfide)
Chlorine then reacts w/ ammonia to produce chloramines (mono,di and tri)
Chloramines are then oxidized which produces nitrous oxide, nitrogen and nitrogen trichloride
Breakpoint occurs
Freely available chlorine

## Slide 11: Chlorine Curve
See Fig 6-14 of your book (page 146)

## Slide 12: Oxidation
Chlorine is a strong oxidizer and can also be used for iron and manganese removal

## Slide 13: Providing a residual
A chlorine residual is usually provided to prevent overgrowth in the piping systems beyond the treatment plant
Also chlorine is used to disinfect new equipment, repaired equipment, etc.

## Slide 14: Chlorine By-Products
THM’s (trihalomethanes)
HAA5 (haloacetic acids)
NDMA (N-nitrosodimethyalmine)-formed from a reaction with dimethylamine when recycling wastewater
All are suspected carcinogens

## Slide 15: Minimizing By-Products
Improve clarification process
Add activated carbon
Use alternative disinfectants
Apply chlorine at later stages (after filtration)

## Slide 16: Other disinfectants
Chlorine dioxide (potential formation of toxic chemicals and high cost; however, doesn’t react with ammonia and doesn’t form THM’s)
Ozone (high cost; doesn’t provide residual; however, ozone doesn’t form THM’s and may remove other toxic trace organic chemicals)
Ultraviolet Radiation (no chemicals; can supplement chlorine; inactivates cryptosporidium)

## Slide 17: Disinfection C*t Product
Inactivating pathogens is a function of the chemical concentration (C) and the time of contact (t)

## Slide 18: Determining C*t values in water treatment
EPA Guidance Manual describes procedure
C*t is determined by summing C*t for tanks, reservoirs, and piping before it arrives to the first customer
C is the free chlorine residual measured at the end of each chlorination segment (mg/l)
t is the calculated contact time of the segment in minutes

## Slide 19: Contact Time
Contact time in reservoirs or tanks is not usually the detention time (short-circuiting and back-mixing)
Tracer study is usually used and the contact time is determined when 10% of the tracer has passed through the reservoir

## Slide 20: Tracer Study using Fluoride

## Slide 21: Surface Water Disinfection
EPA requires 99.9% (3 log) removal of Giardia cysts, 99% (2 log) of Cryptosporidium and 99.99% (4 log) removal of enteric viruses
Filtration is the major method used to get these removal rates
Very rarely is unfiltered water allowed for a community water system

## Slide 22: Groundwater Disinfection
Groundwater not under the influence of surface water may or may not be disinfected

## Slide 23: Ion Exchange
Used for softening
Used for removal of specific contaminants (nitrate)

## Slide 24: Removal of Dissolved Salts
Distillation http://www.excelwater.com/eng/bottling/water-treatment-commercial-distillation.php
Reverse Osmosis http://www.hcti.com/sm/aboutro/aboutro.html
Electrodialysis http://www.fumatech.com/EN/Membrane-technology/Membrane-processes/Electrodialysis/
Reject brine is treated via evaporating ponds, deep-well injection, or piping to the ocean

## Slide 25: Sources of Wastes
Coagulation/Iron & Manganese Removal Wastes
Filter Backwash Water

## Slide 26: Waste Treatment Processes
Lagoons
Drying Beds
Gravity Thickening
Centrifugation
Pressure Filtration

## Slide 27: Freeboard (waves/backup/sloshing)