CTC 450 Standards

Recommended Standards for Water Works pages 171-172, 7th edition:

Water Treatment (rapid mixing);

Rapid Mixing detention time: <30 seconds

Water Treatment (floc formation)

Floc basin detention time >30 minutes

Floc basin flow through velocity (0.5-1.5 ft/min)

Water Treatment (sedimentation)

Sedimentation basin detention time >4 hour (2 by approval)

Sedimentation basin horizontal velocity is <=0.5 ft/min

Sedimentation overflow rate is usually 500-800 gpd/sq ft

Sedimentation weir loading is less than 20,000 gpd/square ft

Wastewater Treatment (primary clarifier) Table 11-2 page 303; EPA standards

| Average Monthly Overflow Rate: 800-1200 gpd/sq ft Side Water Depth: (10-13ft) Weir Loading: 10,000-40,000 gpd/ft | Peak Flow Overflow Rate: 2000-3000 gpd/sq ft Side Water Depth: (10-13ft) Weir Loading: 10,000-40,000 gpd/ft |
| --- | --- |

Wastewater Treatment (primary clarifier) Table 11-2, page 303; Waterworks stds

| Average Monthly Overflow Rate: <1000 gpd/sq ft Side Water Depth: 7’ Weir Loading: <10,000 gpd/ft | Peak Flow Overflow Rate: <1500 gpd/sq ft |
| --- | --- |

Wastewater Treatment (intermediate clarifier) Typical; page 305

Overflow Rate: <1000 gpd/sq ft

Side Water Depth:  >7’

Weir Loading: <20,000 gpd/ft

Wastewater Treatment (secondary or final clarifier) Typical; page 305

Overflow Rate: <800 gpd/sq ft

Side Water Depth:  >7’

Weir Loading: <20,000 gpd/ft

Wastewater Treatment (trickling filter-high stage and not “two-stage”) Table 11-3

Recirculation Ratio (0.5-3)

BOD Loading: 30-90 #/1000 cubic ft/day (or 1300-3900 #/acre-ft/day)

Hydraulic Loading: 10-30 million gallons/acre-day (or 0.16-0.48 gpm/sq ft)